## Questionnaire-Metal castings an
Technical and Operational Diagnostic Questionnaire
Section A- Furnace and Thermal Systems
Question no. | Question | Response | Trigger logic
1 | What type of melting and heat treatment furnace do you use? | Gas-fired furnace
2 | Total number of furnaces
3 | Number of Cupola furnaces |  | Cupola (coke fired) → Recommend transition to gas fired furnace>Induction furnace
4 | Average age of Cupola furnaces |  | >20 years → Efficiency retrofit / replacement feasibility
5 | Number of oil-fired furnaces |  | Oil-fired → Recommend trasition to gas-fired>Induction furnace
6 | Average age of oil-fired furnaces |  | >20 years → Efficiency retrofit / replacement feasibility
7 | Number of gas-fired furnaces |  | Gas fired---> Recommend electrification
8 | Average age of gas-fired furnaces |  | >20 years → Efficiency retrofit / replacement feasibility
9 | Number of induction furnaces |  | No induction furnace----> Recommend transition to induction furnace
10 | Average age of induction furnaces |  | >20 years induction → Recommend high-frequency upgrade
11 | Is waste heat recovery installed on furnaces? |  | No WHR→ Recommend WHR (e.g. recuperator)
12 | Number of furnaces in which waste heat recovery installed |  | Not relevant for induction furnace, since there is no flue gas generation that can be used for recovering waste heat
13 | Do you use oxygen enrichment and combustion optimization methods to improve your energy efficiency? |  | Recommendations will be given if the company responds 'No'.
14 | Is temperature monitoring automated? |  | Manual → Digital controls upgrade
Section B- Motors and Drives
Question no. | Question | Response
1 | What type of motors are installed at your facility? |  | IE1/IE2 → Motor upgrade recommendation/ Unknown motor class→ Motor audit
2 | Are VFDs installed on electrical equipment? | Yes | No VFD → VFD retrofit initiative
3 | Number of equipment in which VFD is installed
4 | Number of equipment in which VFD installation is possible but yet not installed
Section C- Compressed Air System
Question no. | Question | Response
1 | Total number of compressors
2 | Type of compressors used |  | Reciprocating → VSD Screw compressor upgrade
3 | Number of reciprocating compressors |  | Fixed speed screw----> Installation VFD/ VSD screw upgrade
4 | Average age of reciprocating compressors |  | VSD screw---> upgrade to centrifugal (only if high loads required)
5 | Number of fixed-speed screw compressors
6 | Average age of fixed-speed screw compressors
7 | Number of VSD screw compressors
8 | Average age of VSD screw compressors
9 | Number of centrifugal compressors
10 | Average age of centrifugal compressors
11 | Number of other type of compressors
12 | Average age of other type of compressors
13 | Do you have leak management system for your compressed air system? |  | No monitoring → Leak detection system
Section D- Cooling and Utilities
Question no. | Question | Response
1 | What type of cooling system do you have? | Cooling tower | Open loop → Closed-loop conversion
2 | Do you have cooling tower fans |  | Conventional chiller → PHE optimization
Section E- Renewable Energy and Procurement
Question no. | Question | Response
1 | Do you use renewable energy? |  | No RE → Recommed Rooftop Solar or purchase of RE
Secrion F- Digital & Energy Management
Question no. | Question | Response
1 | Do you have an Energy Management System that is ISO 50001 certified? |  | No ISO → Energy management system roadmap
2 | Do you have sub-meters installed at process level/ individual production line? |  | No submetering → Digital monitoring initiative
Section G- Production and Scrap
Question no. | Question | Response
1 | What is your yield loss in %? |  | High yield loss%----> Process Optimization
2 | What is your re-melt rate in %? |  | High re-melt rate----> Process optimization
Section H- Diesel Generators
Question no. | Question | Response
1 | Do you have diesel generators?
2 | Number of DG sets
3 | Do you have DG sets with power rating of >200 kVA?
4 | Do you have diesel-PNG dual fuel kits installed in your DG sets? |  | If diesel-PNG dual kit is not installed---> consider installing dual fuel kits in DG sets

## Initiatives logic database
Asset Type | Condition | Question | Threshold | Recommendation | Scope | Capex Benchmark | Energy Savings | Payback
Motor | Motor efficiency ≤ IE2 | How many IE2 motors with power rating greater than 5 kW operate at your facility? | Power ≥5 kW AND Hours ≥3000 | Replace with IE3/IE4/IE5 motor | Scope 2 | ₹7,000–10,000/kW | 5–10% | 2–4 yrs
Motor | Motor efficiency ≤ IE2 | What are the annual operating hours of IE2 motors? Provide for each such motor. | Power ≥5 kW AND Hours ≥3000 | Replace with IE3/IE4/IE5 motor | Scope 2
Pump/Fan | Variable load AND no VFD | How many pumps operate on variable load at your facility? | Power ≥7.5 kW AND variable load | Install VFD | Scope 2 | ₹4,000–8,000/kW | 20–40% | 1–3 yrs
Pump/Fan | Variable load AND no VFD | How many pumps with power rating greater than 7.5 kW are functioning at your facility? | Power ≥7.5 kW AND variable load | Install VFD | Scope 2
Pump/Fan | Variable load AND no VFD | How many pumps with power rating greater than 7.5 kW have VFD installed? | Power ≥7.5 kW AND variable load | Install VFD | Scope 2
Motor | Frequent idle operation | What are the typical idle operating hours of the motors installed at your facility? | Hours ≥2500 | Install auto shut-off / idle control | Scope 2 | ₹50k–₹2L | 5–15% | <2 yrs
Compressor | Leak audit not conducted | Do you conduct a leak detection and repair program at your facility on regular basis? | No LDAR | Conduct leak detection & fixing | Scope 2 | Part of overall site maintenance | NA | NA
Compressor | Demand variability high | How many fixed speed screw compressors are installed at your facility? | Fixed speed compressor | Install VSD compressor | Scope 2 | ₹8L–₹30L | 20–35% | 2–4 yrs
Compressor system | Pressure fluctuations | Do you have intelligent flow controller installed in your compressor systems? | No flow controller | Install intelligent flow controller | Scope 2 | ₹5L–₹15L | 10–25% | 1–3 yrs
Furnace | Fuel combustion furnace | Do you have oxy-fuel burners installed in your furnaces? | No | Install oxy-fuel burners | Scope 1
Furnace | Fuel combustion furnace | Do you have magnetic resonators installed for fuel magnetic conditioning in your furnace burners? | No | Install magnetic resonators | Scope 1
Furnace | Fuel combustion furnace | Do you have any of these high efficiency burners installed in your furnaces - regenerative burners, low NOx burners or pulse firing burners? | No | Install high efficiency burners | Scope 1
Furnace | Fuel combustion furnace | Do you have automatic combustion system (like O2 trim control) installed in your furnace? | No | Install O2 trim control system | Scope 1 | ₹2L–₹10L | 5–10% | 1–2 yrs
Furnace | Exhaust temp high | What is the flue gas/exhaust gas temperature from your furnace? | If flue gas temperature >400°C | Waste heat recovery system | Scope 1 | ₹20L–₹2Cr | 10–25% | 2–4 yrs
Furnace | Exhaust temp high | Do you have a waste heat recovery system installed in your furnace? | No | Waste heat recovery system | Scope 1
Furnace | Fossil fuel furnace | How many furnace oil furnaces are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Induction furnace | Scope 1 | Site specific | https://docs.google.com/spreadsheets/d/1y_7USpWFmeh3RAkzC-bHZ1ffTl8MBB0PZiUmP3LJlUk/edit?gid=1201408005#gid=1201408005
Furnace | Fossil fuel furnace | How many diesel furnaces are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Induction furnace | Scope 1 | Site specific
Furnace | Fossil fuel furnace | How many coal fired furnaces are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Induction furnace | Scope 1 | Site specific
Boiler | Fossil fuel boiler | Do you have any of these high efficiency burners installed in your boilers - low NOx burners, high turndown burners, O2 trim control system? | No | Install high efficiency burners | Scope 1
Boiler | Fossil fuel boiler | What is the flue gas/exhaust gas temperature from your boiler? | If flue gas temperature >400°C | Waste heat recovery boiler | Scope 1 | ₹20L–₹2Cr | 10–25% | 2–4 yrs
Boiler | No economizer | Do you have economizer/s installed in your boilers for waste heat recovery? | No | Install economizer | Scope 1 | ₹5L–₹20L | 5–12% fuel savings | 1–3 yrs
Boiler | Fossil fuel boiler | How many furnace oil boilers are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Electric boiler | Scope 1 | Site specific | https://docs.google.com/spreadsheets/d/1y_7USpWFmeh3RAkzC-bHZ1ffTl8MBB0PZiUmP3LJlUk/edit?gid=1201408005#gid=1201408005
Boiler | Fossil fuel boiler | How many diesel boilers are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Electric boiler | Scope 1 | Site specific
Boiler | Fossil fuel boiler | How many coal fired boilers are installed at your facility? | Coal/FO/diesel | Switch to Biofuel/PNG/LPG/Electric boiler | Scope 1 | Site specific
Boiler | Manual blow down | Do you have manual blowdown management for your boilers? | Yes | Install automatic blowdown system | Scope 1 or Scope 2
Electrical system | Power factor <0.95 | Have you installed APFC (Autotmatic Power Factor Correction) panel for improving the electrical efficiency of the equipments at your facility? | No | Install APFC panel | Scope 2 | ₹1L–₹5L | 5–10% bill savings | 1–2 yrs
Lighting | Non LED | Have you installed LED lights for lighting requirements at your facility? | No | LED light installation | Scope 2 | ₹300–₹800/fixture | 40–60% | <1 yr
Fans | Conventional ceiling fans | Do you have conventional ceiling fans at your facility? If yes, please mention the number of such fans. | Yes | Install BLDC fans | Scope 2 | ₹2500-3500/fan | 55–65% energy/emissions savings | 1–2 yrs
Solar/Wind power | Roof space available | Have you ever conducted a feasibility study to estimate rooftop solar requirements for your facility? | No | Feasibility study is recommended to ascertain requirement of rooftop solar | Scope 2 | ₹40k–₹55k/kW | 20–40% Scope 2 reduction | 4–6 yrs
Facility | High electricity consumption | Is your required load greater than 1 MW? | >1 MW load | Purchase open access renewable power to cut down Scope 2 emissions | Scope 2 | Contract based | Up to 100% renewable electricity | 3–5 yrs

## FurnaceBoiler - Fuel switch
Emissions savings calculation due to fuel switch in furnaces
Existing fuel | Upgrade to | EF of existing fuel (kgCO2e/kWh Net CV) Source: DEFRA 2025 | EF of upgraded fuel (kgCO2e/kWh Net CV) Source: DEFRA 2025 | Emissions saved (kgCO2e/kWh Net CV) | Emissions saved (%)
Coke | Furnace Oil | 0.37675 | 0.28523 | 0.09152 | 24.29%
Coke | LPG | 0.37675 | 0.23032 | 0.14643 | 38.87%
Coke | LNG | 0.37675 | 0.20489 | 0.17186 | 45.62%
Coke | PNG | 0.37675 | 0.20489 | 0.17186 | 45.62%
Coke | Biodiesel | 0.37675 | 0.018215 | 0.35854 | 95.17%
Coke | Compressed biomethane | 0.37675 | 0.0003825 | 0.37637 | 99.9%
Coke | Liquefied biomethane | 0.37675 | 0.0003825 | 0.37637 | 99.9%
Furnace Oil | LPG | 0.28523 | 0.23032 | 0.05491 | 19.25%
Furnace Oil | LNG | 0.28523 | 0.20489 | 0.08034 | 28.17%
Furnace Oil | PNG | 0.28523 | 0.20489 | 0.08034 | 28.17%
Furnace Oil | Biodiesel | 0.28523 | 0.018215 | 0.26702 | 93.61%
Furnace Oil | Compressed biomethane | 0.28523 | 0.0003825 | 0.28485 | 99.87%
Furnace Oil | Liquefied biomethane | 0.28523 | 0.0003825 | 0.28485 | 99.87%
Emissions savings calculation for shifting from FO-fired billet heating furnace to induction billet heating furnace
FO required (kg/ton of billet) | 162 | Reference
EF of FO (kgCO2e/kg) Source: IPCC | 3.4 | DETAILED PROJECT REPORT MICRO TURBINE
Emissions (kgCO2e/ton of billet) | 550.8
Electrcity consumed (kWh/ton of billet) | 658
Grid EF (kgCO2e/ kWh) | 0.716
Emissions (kgCO2e/ton of billet) | 471.128
Emissions saved (kgCO2e/ton of billet) | 79.672
Emissions saved (%) | 14.46%

## Motor upgrade - emissions savin
[5 empty] | Motor class | Baseline motor efficiency |  | User provided motor efficiency | Default capex - Least | Default capex - Max | User provided capex
` | Units | Input example | Notes |  |  | Least | Max | (If available with user) | (in INR/kW) | (in INR/kW) | (If available with user)
Current motor make and model | Text | Name of company and model | To be selected by user from dropdowns
Motor name | Text | XX2345 | User input |  | IE1 | 75% | 85% | User input | 3500 | 4500
Motor rating | kW | 0.37 | Units (HP/kW) to be decided by the user |  | IE2 | 85% | 89% | User input | 4000 | 5000
Current motor efficiency class | - | IE2 | User input |  | IE3 | 90% | 94% | User input | 4800 | 6200
Target motor efficiency class | - | IE3 | User input |  | IE4 | 94% | 96% | User input | 6000 | 8000
Load factor (%) | Percentage | 80% | User input (default value is 80%) |  | IE5 | 96% | 97% | User input | 9000 | 12000
Operating hours/year | Number of hours/year | 8000 | User input
Electricity tariff | INR/kWh | 8 | User input
Grid emission factor | kgCO₂e/kWh | 0.71 | Default India Grid Emission factor
Number of motors to be upgraded | Number | 5 | User input
Capex of current motor class | INR/kW | 4000 | User input
Capex of target motor class | INR/kW | 4800 | User Input
Number of years of operation of current motor class | years | 5 | User input
Lifetime of target motor class | years | 10 | Default is 10. Can be user input.
Calculation
Rater power of current motor class | kW | 0.37 | If motor rating is given in HP, then use the formula given in the cell. Else, the motor rating will be the same as given in the table above.
Input power required for current motor class | kW | 0.43529 | Based on baseline motor efficiency - Least | 3.73
Annual energy consumption for current motor class | kWh | 3482.3529
Input power for target motor class | kW | 0.38542 | Based on baseline motor efficiency - Least
Annual energy consumption for target motor class | kWh | 3083.3333
Annual energy savings | kWh | 399.0196
Annual GHG emissions savings | kgCO2e/year | 283.3039 | 2833.0392
Annual energy cost savings | INR/year | 3192.1569
Present value of current motor class | INR | 2636.3261 | Discount factor assumed is 8%
Incremental cost for motor upgrade per motor | INR/kW | 2163.6739 | Based on baseline capex - least
Net Present Value of energy cost savings over lifetime of target motor | INR | 21419.6324
Payback period | years | 0.67781
Net Present Value of emissions reduced over lifetime of target motor class | kgCO2e | 1900.9924
Marginal Abatement Cost (per motor per kW) | INR/kgCO2e | -10.1294 | =(Incremental cost for motor upgrade - NPV (Lifetime energy cost savings))/NPV (Lifetime emissions reduced)

## Compressor
Compressor Type | Typical Specific Power | Equivalent Efficiency Range | Default value to be taken (lower value of the equivalent efficiency range) | Notes
Reciprocating (Piston) | 5.5 – 7.5 kW/m³/min | ~65–75% | 65% | Good for small loads and intermittent use
Fixed Speed (Rotary Screw) | 6.0 – 7.0 kW/m³/min | ~70–80% | 70% | Most common in industry
Variable Speed Drive (Rotary Screw) | 5.0 – 6.0 kW/m³/min | ~80–90% | 80% | Best for variable demand
Centrifugal | 4.5 – 5.5 kW/m³/min | ~80–90% | 80% | Efficient at large capacity
Scroll Compressors | 5.5 – 6.5 kW/m³/min | ~70–80% | 70% | Used in small systems
Oil-free Screw | 6.5 – 8.0 kW/m³/min | ~65–75% | 65% | Lower efficiency but high purity air | Equipment | Typical Lifetime
[5 empty] | Compressor replacement | 10–15 years
[5 empty] | VSD retrofit | 8–12 years
Data | Description |  |  |  | Control system upgrade | 8–10 years
Field | Units | Input example | Notes
Current compressor make and model | - | Name of company and model | User input or net scraping
Rated capacity | kW | 2.2 | Units (HP/kW) to be decided by the user
Current compressor type | - | Fixed speed (Rotary screw) | User input
Age of current compressor | years | 4 | User input
Target compressor type | - | Variable Speed Drive (Rotary Screw) | User input
Rated capacity - target compressor | kW | 2.2
Lifetime of target compressor | years | 10 | Default is 10. Can be user input also.
Load factor (%) | Percentage | 80% | User input (default value is 80%)
Operating hours/year | Number of hours/year | 8000 | User input
Electricity tariff | INR/kWh | 8 | User input
Grid emission factor | kg CO₂/kWh | 0.716 | Default India Grid Emission factor
Energy consumption | kWh/year | 2400 | User input | 14080
Capex of current compressor type | INR | 35200 | User input or net scraping | 112640
Discount rate | % | 8% | Default value of 8% is used
Basline energy consumption | kWh | 21661.5385 | If Rated power is given in HP, then the value will be | =Rated power in HP * 0.746 * Operating hours * Load factor
Target energy consumption | kWh | 17600
Annual energy savings | kWh | 4061.5385
Annual energy cost savings | INR | 32492.3077
Annual emission savings | kgCO2e | 2908.0615
Present value of current compressor | INR | 25217.0322
Capex of target compressor type | INR | 352000
Incremental cost for compressor upgrade | INR | 326782.9678
Net Present Value of energy cost savings over lifetime of target compressor | INR | 218026.0295
Net Present Value of emissions reduced over lifetime of target compressor | kgCO2e | 19513.3296
Payback period | years | 10.0572
Marginal abatement cost per target compressor | INR/kgCO2e | 5.5735 | <0 means compressor upgrade saves money during lifetime
Marginal abatement cost formula | (Incremental cost for compressor upgrade - NPV(Lifetime energy cost savings))/NPV(Lifetime emissions reduced)

## Air conditioner
[7 empty] | 1 TR | =3.517 kW
Typical cost of fixed speed split AC in India | air conditioner star rating | Typical ISEER range | Approximate annual electricity consumption (kWh/year) | Default ISEER for split AC (invertor & fixed speed) | Default ISEER for window AC | Default ISEER for Standing tower AC | Default ISEER for Casette type AC | Default ISEER for Corner/Floor mounted AC
25000-40000 | 1 star | 3.1 | 1500-1600 | 3.1 | 2.7 | 2.9 | 3.1 | 2.9
26990-38690 | 2 star | 3.3-3.5 | 1350-1450 | 3.3 | 2.8 | 3 | 3.2 | 3
28000-40000 | 3 star | 3.9 | 1150-1250 | 3.9 | 3.2 | 3.6 | 3.6 | 3.6
30000-45000 | 4 star | 4.5 | 1000-1050 | 4.5 | 3.6 | 4 | 4 | 4
28000-45000 | 5 star | 5.0-5.2 | 850-900 | 5.2 | 4.1 | 4.6 | 4.6 | 4.6
| Field | Units | Input | Notes
| Current AC make and model | - | Name of company and model | User input
| Cooling capacity of current AC | TR | 1.5 | User input.
| Current AC type | - | Split - Fixed speed | User input
| Age of current AC | years | 6 | User input
| Current AC star rating | 1 to 5 star | 3-star | User input
| Number of hours of operation of AC | hours/year | 2400 | Default is 8 hours for 300 days in a year. User input can also be used.
| Target AC type | - | Split - Invertor | User input
| Rated capacity - target AC | TR | 1.5 | User input
| Target AC star rating | 1 to 5 star | 4-star | User input
| Lifetime of target AC | years | 15 | Default is 15. Can be user input also.
| Load factor (%) | Percentage | 80% | User input (default value is 80%)
| Operating hours/year | Number of hours/year | 8000 | User input
| Electricity tariff | INR/kWh | 8 | User input
| Grid emission factor | kg CO₂/kWh | 0.71 | Default India Grid Emission factor
| Capex of current air conditioner type | INR | 29000 | User input
| Capex of target air conditioner type | INR | 42000 | User input
| Discount rate | % | 8% | Default value of 8% is used
| Current AC cooling output | kWh | 12661.2 | Cooling output = Cooling capacity (in TR) * Operating hours * 3.517 | If cooling capacity is given in TR, then the formula is as given. If cooling capacity if given in kW, then formula is Cooling output = Cooling capacity (in kW) * operating hours
| Current AC electricity consumption | kWh | 3836.7273 | Electricity consumption = Cooling output/ISEER
| Target AC electricity consumption | kWh | 2813.6
| Annual energy savings | kWh | 1023.1273
| Annual energy cost savings | INR | 8185.0182
| Annual emission savings | kgCO2e | 726.4204
| Present value of current air conditioner | INR | 17584.295
| Incremental cost for air conditioner upgrade | INR | 24415.705
| Net Present Value of energy cost savings over lifetime of target air conditioner | INR | 70059.4887
| Net Present Value of emissions reduced over lifetime of target air conditioner | kgCO2e | 6217.7796
| Payback period | years | 2.983
| Marginal abatement cost per target air conditioner | INR/kgCO2e | -7.3408
| Marginal abatement cost formula | (Incremental cost for air conditioner upgrade - NPV(Lifetime energy cost savings))/NPV(Lifetime emissions reduced)

## BLDC fans-emissions savings
Emissions savings by switching from conventional induction motor fans to BLDC (Brushless Direct Current) fans
Conventional induction motor fan model |  | User input
Power rating of a conventional induction motor fan (W) | 74 | User input
Energy consumption per hour (kWh) | 0.074
Daily runtime (hours) | 12 | User input
Number of working days in a year | 250 | User input
Annual runtime (hours) | 3000
Annual energy consumption per fan (kWh) | 222
Electricity tariff (INR/kWh) | 8 | User input
Annual energy expenditure per fan (INR) | 1776
Grid EF (kgCO2e/kWh) | 0.716 | Default
Emissions (kgCO2e) per fan | 158.952
BLDC fan model |  | User input
Power rating of a BLDC fan (W) | 24 | Source: https://www.crompton.co.in/blogs/fans-guide/bldc-fans-vs-normal-fans
Energy consumption per hour (kWh) | 0.024
Annual energy consumption per fan (kWh) | 72
Emissions (kgCO2e) per fan | 51.552
Annual energy expenditure per fan (INR) | 576
Calculating annual cost and emissions reduced
Annual energy cost savings per fan (INR) | 1200
% of energy costs saved per fan | 67.57%
Annual emissions reduced per fan (kgCO2e) | 107.4
Emissions saved per fan (%) | 67.57%
Number of conventional fans to be switched to BLDC fans | 20 | User input
Total cost savings per annum (INR) | 24000
Total emissions saved per annum (kgCO2e) | 2148
Calculating payback period
Capex for BLDC fan (INR per fan) | 4500 | User input
Total capex required for switching to BLDC fans (INR) | 90000
Payback period (years) | 3.75
Calculating Marginal Abatement Cost (MAC)
Capital cost for installing BLDC fan (INR per fan) | 4500 | Default/user input
Capital cost for installing conventional induction motor fan (INR per fan) | 2000 | Default/user input
Current years of operation of conventional fan | 2 | user input
Discount factor | 8% | Default/user input
PV of conventional fan (INR per fan) | 1692.8
Incremental cost (INR per fan) | 2807.2 | Capex of BLDC - PV of conventional fan
Typical lifetime of BLDC fan (years) | 10 | Default/user input
NPV of energy cost savings during the lifetime per fan (INR) | 8052.0977
NPV of emissions saved during the lifetime (kgCO2e) per fan | 720.6627
MAC (INR/kgCOe2) | -7.2779

## LED retrofit-emissions savings
Emissions savings by switching from incandescent bulbs to LEDs
Conventional incandescent bulb model |  | User input
Power rating of a conventional incandescent bulb (W) | 60 | User input
Energy consumption per hour (kWh) | 0.06
Daily runtime (hours) | 12 | User input
Number of working days in a year | 250 | User input
Annual runtime (hours) | 3000
Annual energy consumption per bulb (kWh) | 180
Electricity tariff (INR/kWh) | 8 | User input
Annual energy expenditure per bulb (INR) | 1440
Grid EF (kgCO2e/kWh) | 0.716 | Default
Emissions (kgCO2e) per bulb | 128.88
LED model |  | User input
Power rating of an LED (W) | 7 | Source:
Energy consumption per hour (kWh) | 0.007
Annual energy consumption per LED (kWh) | 21 |  | 1.56
Emissions (kgCO2e) per LED | 15.036
Annual energy expenditure per LED (INR) | 168
Calculating annual cost and emissions reduced
Annual energy cost savings per LED (INR) | 1272
% of energy costs saved per LED | 88.33%
Annual emissions reduced per LED (kgCO2e) | 113.844
Emissions saved per LED (%) | 88.33%
Number of conventional incandescent bulbs to be switched with LEDs | 50 | User input
Total cost savings per annum (INR) | 63600
Total emissions saved per annum (kgCO2e) | 5692.2
Calculating payback period
Capital cost for installing LED (INR per LED) | 165 | User input
Total capex required for switching to LEDs (INR) | 8250
Payback period (years) | 0.12972
Calculating Marginal Abatement Cost (MAC)
Capital cost for installing LED (INR per LED) | 165 | Default/user input
Capital cost for installing conventional incandescent bulb (INR per bulb) | 20 | Default/user input
Current years of operation of incandescent bulb | 5 | user input
Discount factor | 8% | Default/user input
NPV (conventional fan) | 13.1816
Incremental cost (INR per bulb) | 151.8184 | Capex of BLDC - NPV of conventional fan
Typical lifetime of LED (years) | 20 | Default/user input
NPV of energy cost savings during the lifetime (INR) per LED | 12488.6835
NPV of emissions saved during the lifetime (kgCO2e) per LED | 1117.7372
MAC (INR/kgCOe2) | -11.0374

## Dual fuel kit retrofit in DG se
| DG model |  |  | user input |  |  |  |  | Load | Typical SFC | Least | Most | Average (Default to be taken by the calculation engine)
| DG manufacturer |  |  | user input |  |  |  |  | 25% load | 0.32 – 0.38 L/kWh | 0.32 | 0.38 | 0.35
| Rated capacity of the DG set | 48 | kVA | user input |  |  |  |  | 50% load | 0.27 – 0.30 L/kWh | 0.27 | 0.3 | 0.285
| Do you have annual diesel consumption data for DG set? | No | Yes/No | user input |  |  |  |  | 75% load | 0.24 – 0.27 L/kWh (most efficient) | 0.24 | 0.27 | 0.255
If Yes -> | Annual diesel consumption | 18168.75 | L | user input |  |  |  |  | 100% load | 0.25 – 0.28 L/kWh | 0.25 | 0.28 | 0.265
If No -> | Average load on DG | 75 | % | user input
| Power factor | 0.95 | Default is 0.95 | user input |  |  |  |  | Fuel | Substitution
| Average load on DG | 34.2 | kVA | calculated |  |  |  |  | CNG/PNG | 70–80%
| Operating hours per year | 750 | hours | user input |  |  |  |  | LPG | 60–70%
| Annual electricity generated | 25650 | kWh | This can be calculated from rated capacity of DG, average load factor and power factor or a user input |  |  |  |  | Biogas | 50–65%
|  | 0.26 | L/kWh | user input
| Annual diesel consumption | 6669 | L | calculated
Calculation (before retrofit)
| Annual diesel consumption (before retrofit) | 19023.75 | L
| Net CV of diesel | 9.927 | kWh/L | Default NCV of diesel taken from DEFRA 2025
| Annual energy consumption (before retrofit) | 188848.7663 | kWh | calculated
| Annual emissions (before retrofit) | 50632.6618 | kgCO2e | calculated | EF of diesel | 2.6616 | kgCO2e/L | default emissions factor for diesel taken from DEFRA 2025
| Total cost incurred due to diesel consumption in DG set (before retrofit) | 1712137.5 | INR | calculated | Diesel Rate | 90 | INR/L | user input/default
13316.625
| Calculation (after retrofit) |  |  |  | Fuel | NCV | UoM | Source
| Type of fuel replacement using duel fuel kit | CNG |  | user input | PNG | 0.01 | kWh/L | DEFRA 2025
| Percentage of diesel replaced after retrofit | 70 | % | user input | CNG | 2.224 | kWh/L | DEFRA 2025
| Annual diesel consumption (after retrofit) | 5707.125 | L | calculated | LPG | 6.761 | kWh/L | DEFRA 2025
| Total energy consumption from diesel (after retrofit) | 56654.6299 | kWh | calculated
| Total energy consumption from other fuel (after retrofit) | 132194.1364 | kWh | calculated
| Net CV of other fuel | 2.224 | kWh/L | Linked to table
| Annual consumption of other fuel (after retrofit) | 59439.8095 | L | calculated
| Annual emissions due to consumption of diesel in DG set (after retrofit) | 15189.7985 | kgCO2e | calculated | Fuel | EF | UoM | Source
| Annual emissions due to consumption of other fuel in DG set (after retrofit) | 26789.5222 | kgCO2e | calculated | PNG | 0.0020891 | kgCO2e/L | DEFRA 2025
| Total emissions (after retrofit) | 41979.3207 | kgCO2e | calculated | CNG | 0.4507 | kgCO2e/L | DEFRA 2025
| Total cost incurred due to diesel consumption in DG set (after retrofit) | 513641.25 | INR | calculated | LPG | 1.5571 | kgCO2e/L | DEFRA 2025
| Total cost incurred due to other fuel consumption in DG set (after retrofit) | 832157.3333 | INR | calculated
| Total cost incurred due to fuel consumption in DG set (after retrofit) | 1345798.583 | INR | calculated
| Annual emissions saved/reduced | 8653.3411 | kgCO2e | calculated | Fuel | Rate | UoM | Source
| Annual emissions saved/reduced % | 17.0904 | % | calculated | PNG | 0.055 | INR/L | Fuel Prices Today [12 March, 2026]: Petrol & Diesel Steady Despite Crude Spike to $98; LPG Up ₹60, CNG Edges Higher ¦ Check City-Wise Rates
[5 empty] | CNG | 14 | INR/L
| Calculation of cost savings |  |  |  | LPG | 32 | INR/L
| Annual cost savings | 366338.9167 | INR | calculated
| Annual cost savings in % | 21.3966 | % | calculated
Calculation of payback period
| Capex of installing dual fuel kit (cost of kit+installation) | 450000 | INR | user unput
| Annual maintenance cost due to the installation of dual fuel kit | 20000 | INR | user unput
| Payback period | 1.2993 | years | calculated
Calculation of MAC
| Capex of installing dual fuel kit (cost of kit+installation) | 450000 | INR | Default/user input
| Typical lifetime of dual fuel kit | 10 | years | Default/user input
| NPV of maintenance cost over lifetime of retrofitted asset | 134201.628 | INR | calculated
| Discount factor | 8% |  | Default/user input
| NPV of cost savings during the lifetime per kit | 2458163.951 | INR | calculated
| NPV of emissions saved during the lifetime per kit | 58064.6233 | kgCO2e | calculated
| MAC | -32.2737 | INR/kgCOe2 | calculated
5806.4623

## AL Supplier Analysis-Pilot
Name of the supplier | Scope 1 emissions (tCO2e) | Scope 2 emissions (tCO2e) | Scope 3 emissions (tCO2e) | Scope 1 +Scope 2 emissions (tCO2e) | Contribution of Scope 2 in Scope 1+Scope 2 | Emissions intensity (kgCO2e/ INR 100000)
PADMAVATI CASTINGS PRIVATE LIMITED | 9.12 | 6642.01 | 12119.07 | 6651.13 | 99.86% | 9.32
FERRO LINKS | 40.84 | 4918.51 | 14507.22 | 4959.35 | 99.18% | 30.7
DIGHVIJAY PLASTICS AND ALLIED | 620.79 | 2236.06 | 12040.19 | 2856.85 | 78.27% | 8.69
SUYESH IRON & STEEL PRIVATE LIMITED | 9.92 | 589.47 | 10313.49 | 599.39 | 98.34% | 12.1
RSM AUTOKAST PRIVATE LIMITED | 51.53 | 1049.31 | 9454.15 | 1100.84 | 95.32% | 9.04

## AL supplier decarbonization rec
Name of the supplier | Scope 1 emissions (tCO2e) | Scope 2 emissions (tCO2e) | Scope 3 emissions (tCO2e) | Scope 1 +Scope 2 emissions (tCO2e) | % ShareOF SCOPE 2 | Complexity of implementing initiative | Rationale
PADMAVATI CASTINGS PRIVATE LIMITED | 9.12 | 6642.01 | 12119.07 | 6651.13 | 99.86% | Low complexity | -Low capex -No major infrastructure modifications -Uses existng assets -Minimal production disruption -Proven and matured technology
FERRO LINKS | 40.84 | 4918.51 | 14507.22 | 4959.35 | 99.18% | Medium complexity | -Moderate capex -Partial equipment replacement -Minor infrastructure modification -Requires technical integration -May require vendor dependency
DIGHVIJAY PLASTICS AND ALLIED | 620.79 | 2236.06 | 12040.19 | 2856.85 | 78.27% | High complexity | -High capex -Major infrastructure transformation -Technology risk or dependency -Production redesign or new facility -Heavy regulatory/grid dependency
SUYESH IRON & STEEL PRIVATE LIMITED | 9.92 | 589.47 | 10313.49 | 599.39 | 98.34%
RSM AUTOKAST PRIVATE LIMITED | 51.53 | 1049.31 | 9454.15 | 1100.84 | 95.32%
Name of the supplier | Decarbonization lever | Example Initiative | Potential Benefit | Complexity of implementation based on cost and infrasturctural constraints | Timeline of implementation <1 year- short term 1-3 years- mid term >3 years- long term
PADMAVATI CASTINGS PRIVATE LIMITED FERROLINKS SUYESH IRON & STEEL PRIVATE LIMITED RSM AUTOKAST PRIVATE LIMITED | Energy Audit/Assessment | Consider conducting energy audits every year at each manufacturing facility led either by company's internal operating divisions or third party agents | Energy audits are undertaken to identify opportunities for improved energy efficiency and cost savings across the facility | Low | Short term
| Energy Efficiency | Consider implementing energy conservation initiatives like "Turn Off Turn Down (TOTD)" program to encourage employees to reduce unnecessary energy consumption by making equipment to be switched to standby, low-energy mode, or fully powered down when not in use | These initiatives help to avoid unnecessary energy consumption across the facility and build energy awareness among the employees | Low | Short term
| Energy Efficiency | Consider phasing out inefficient lighting systems and deploying advanced and efficient LED lights | Reduction in energy consumption and cost savings | Low | Short term
| Energy Efficiency | Consider installation of automatic lights/lights with occupancy sensors to optimize the power consumption | Reduction in energy consumption and cost savings | Low | Short term
| Energy Efficiency | Consider phasing out inefficient motors (IE1/IE2) and upgrading pumps, blowers, compressors and other equipment with higher efficiency motors (IE3 / IE4) | Reduction in energy consumption and cost savings | Low | Short term
| Energy Efficiency | Consider installing Variable Frequency Drives (VFDs) on hydraulic motors, compressors, blowers, pumps and other equipment | Reduction in energy consumption and cost savings | Medium | Short term
| Energy Efficiency | Consider installing auto-cut timers/controllers in lighting, heating and cooling appliances in buildings | Reduction in energy consumption and cost savings | Low | Short term
| Energy Efficiency | Consider conversion of motor connections of grinding machines from delta to star configuration. | Reduction in energy consumption and cost savings | Low | Short term
| Energy Efficiency | Consider implementing custom-built heater insulation jackets for furnaces | Reduction in energy consumption and cost savings | Medium | Short term
| Energy Efficiency | Consider implementation of BLDC fans instead of conventional fans | Reduction in energy consumption and cost savings | Medium | Short term
| Renewable electricity | Consider shifting towards renewable electricity sources through the installation of rooftop solar panel or open access PPA | Reduction in emissions and utility cost | High | Mid-term
| Compressed air system optimization | Minimize air leakages to reduce the load on air compressors through conducting regular compressor audits | Reduction in energy consumption and cost savings | Low | Short Term
| Compressed air system optimization | Consider installation of Intelligent Flow Controllers to improve compressed air efficiency | Reduction in energy consumption and cost savings | Low | Short term
| Compressed air system optimization | Consider deploying energy-efficient compressors and Automatic Power Factor Correction (APFC) panels to improve electrical efficiency and power factor | Reduction in energy consumption and cost savings | Medium | Short term
| Compressed air system optimization | Consider deploying pulse nozzles for cleaning of machine parts | Reduction in energy consumption and cost savings | Low | Short Term
| Compressed air system optimization | Consider Installation of VFDs | Reduction in energy consumption and cost savings | Medium | Short term
| Daylighting | Consider replacement of GI Roof Sheets with Transparent Polycarbonate Sheets for maximum daylight utilization, effective for reducing energy consumption in warehouses | Reduction in energy consumption and cost savings | Low | Short term
| Waste Heat Recovery | Consider deploying waste heat recovery system in furnace to improve energy utilization | Reduction in energy consumption and cost savings | Medium to High | Short term

## Electric Truck
Field | Units | Inputs | notes
Annual distance travelled | km/year | 50000 | User input
Diesel truck fuel efficiency | km/l | 4 | User input
Diesel price | INR/l | 90 | User input
Diesel emission factor | kgCO2e/l | 2.6616 | From DEFRA 2025
Electric truck efficiency | km/kWh | 1.5 | User input
Electricity tariff | INR/kWh | 8 | Commercial/industrial rate
Grid emission factor | kgCO2e/kWh | 0.716 | India average
Existing diesel truck
Age of current diesel truck | years | 5 | How long it has been in use
Original purchase price of diesel truck | INR | 2000000 | User input
New electric truck
Purchase price of electric truck | INR | 3500000 | User input
Subsidy / incentive for electric truck | INR |  | User input
Financial parameters
Lifetime of electric truck | years | 15 | User input
Discount rate | % | 8
Diesel consumption | L/Km | 0.25
Electric consumption | kWh/Km | 0.66667
Annual diesel used | Litres | 12500
Annual Electricity used | kWh | 33333.3333
Annual diesel cost | INR | 1125000
Annual Electricity cost | INR | 266666.6667
Annual diesel emission | KgCO2e | 33269.375
Annual Electricity emission | KgCO2e | 23866.6667
Annual energy cost savings | INR | 858333.3333
Annual emissions savings | KgCO2e | 9402.7083
Present value of existing diesel truck | INR | 1318163.046 | Today’s value of old truck: original price (C11) discounted by age (C10) at discount rate
Net cost of new electric truck | INR | 3500000
Incremental capex | INR | 2181836.954 | Extra money needed today.
Annuity Factor |  | 8.5595 | convert annual savings to total present value over lifetime
Net present value of energy cost savings | INR | 7346885.874
Net present value of emissions reductions | KgCO2e | 80482.2816
Payback period | Years | 2.5419
Marginal abatement cost | INR/kgCO2e | -64.1762 | Annual profit from switching 9,402 × 64 = 601,728